## Overview
KC868-A16 MODBUS RTU Register Map | v1.0 (MAP_VERSION=0x0100)
Default Slave ID | 1
Default Serial | 38400 8N1
Word order | U32/FLOAT32 = Low word then High word
Strings | ASCII, 2 chars per register (HighByte then LowByte), null padded
Notes | NModbus4 uses 0-based offsets (e.g., 30001 => offset 0)

## Coils
Ref | Offset (0-based) | R/W | Type | Units/Format | Description
00001 | 0 | R/W | Bool | 0/1 | DO1 MOSFET output
00002 | 1 | R/W | Bool | 0/1 | DO2 MOSFET output
00003 | 2 | R/W | Bool | 0/1 | DO3 MOSFET output
00004 | 3 | R/W | Bool | 0/1 | DO4 MOSFET output
00005 | 4 | R/W | Bool | 0/1 | DO5 MOSFET output
00006 | 5 | R/W | Bool | 0/1 | DO6 MOSFET output
00007 | 6 | R/W | Bool | 0/1 | DO7 MOSFET output
00008 | 7 | R/W | Bool | 0/1 | DO8 MOSFET output
00009 | 8 | R/W | Bool | 0/1 | DO9 MOSFET output
00010 | 9 | R/W | Bool | 0/1 | DO10 MOSFET output
00011 | 10 | R/W | Bool | 0/1 | DO11 MOSFET output
00012 | 11 | R/W | Bool | 0/1 | DO12 MOSFET output
00013 | 12 | R/W | Bool | 0/1 | DO13 MOSFET output
00014 | 13 | R/W | Bool | 0/1 | DO14 MOSFET output
00015 | 14 | R/W | Bool | 0/1 | DO15 MOSFET output
00016 | 15 | R/W | Bool | 0/1 | DO16 MOSFET output
00019 | 18 | R/W | Bool | 0/1 | Outputs Master Enable (0=force all OFF, 1=allow normal control)
00020 | 19 | R/W | Bool | 0/1 | Night mode enable (maps to rs485NightMode)

## DiscreteInputs
Ref | Offset (0-based) | R/W | Type | Units/Format | Description
10001 | 0 | R | Bool | 0/1 | DI1 main digital input
10002 | 1 | R | Bool | 0/1 | DI2 main digital input
10003 | 2 | R | Bool | 0/1 | DI3 main digital input
10004 | 3 | R | Bool | 0/1 | DI4 main digital input
10005 | 4 | R | Bool | 0/1 | DI5 main digital input
10006 | 5 | R | Bool | 0/1 | DI6 main digital input
10007 | 6 | R | Bool | 0/1 | DI7 main digital input
10008 | 7 | R | Bool | 0/1 | DI8 main digital input
10009 | 8 | R | Bool | 0/1 | DI9 main digital input
10010 | 9 | R | Bool | 0/1 | DI10 main digital input
10011 | 10 | R | Bool | 0/1 | DI11 main digital input
10012 | 11 | R | Bool | 0/1 | DI12 main digital input
10013 | 12 | R | Bool | 0/1 | DI13 main digital input
10014 | 13 | R | Bool | 0/1 | DI14 main digital input
10015 | 14 | R | Bool | 0/1 | DI15 main digital input
10016 | 15 | R | Bool | 0/1 | DI16 main digital input
10017 | 16 | R | Bool | 0/1 | Direct GPIO input 1
10018 | 17 | R | Bool | 0/1 | Direct GPIO input 2
10019 | 18 | R | Bool | 0/1 | Direct GPIO input 3
10020 | 19 | R | Bool | 0/1 | Ethernet connected
10021 | 20 | R | Bool | 0/1 | WiFi connected
10022 | 21 | R | Bool | 0/1 | AP mode active
10023 | 22 | R | Bool | 0/1 | Restart required flag
10024 | 23 | R | Bool | 0/1 | Modbus RTU active (stack running + serial ready)

## InputRegisters
Ref | Offset (0-based) | R/W | Type | Units/Format | Description
30001 | 0 | R | U16 | 0x0100 | Register map version
30002 | 1 | R | U16 | bitfield | Device status (reserved/legacy)
30003 | 2 | R | U16 | counter | Heartbeat (increments every 1 second)
30004..30005 | 3..4 | R | U32 | seconds | Uptime seconds (LOW word @30004)
30006 | 5 | R | U16 | counter | Change sequence counter (increments on any snapshot change)
30009 | 8 | R | U16 |  | Last error code (0=OK)
30010..30011 | 9..10 | R | U32 | bytes | Free heap bytes (LOW word @30010)
30012 | 11 | R | U16 | MHz | CPU frequency
30013 | 12 | R | U16 | 0..4095 | AI1 raw
30014 | 13 | R | U16 | 0..4095 | AI2 raw
30015 | 14 | R | U16 | 0..4095 | AI3 raw
30016 | 15 | R | U16 | 0..4095 | AI4 raw
30017 | 16 | R | U16 | mV 0..5000 | AI1 millivolts
30018 | 17 | R | U16 | mV 0..5000 | AI2 millivolts
30019 | 18 | R | U16 | mV 0..5000 | AI3 millivolts
30020 | 19 | R | U16 | mV 0..5000 | AI4 millivolts
30021 | 20 | R | S16 | x10 (0.1°C) | DHT1 temp
30022 | 21 | R | U16 | x10 (0.1%RH) | DHT1 humidity
30023 | 22 | R | S16 | x10 (0.1°C) | DHT2 temp
30024 | 23 | R | U16 | x10 (0.1%RH) | DHT2 humidity
30025 | 24 | R | S16 | x10 (0.1°C) | DS18B20 temp
30026 | 25 | R | U16 | bitfield | Sensor status: bit0=DHT1 ok, bit1=DHT2 ok, bit2=DS18 ok
30027..30028 | 26..27 | R | U32 | unix seconds | RTC UNIX time seconds (LOW word @30027)
30029 | 28 | R | U16 |  | RTC year
30030 | 29 | R | U16 |  | RTC month
30031 | 30 | R | U16 |  | RTC day
30032 | 31 | R | U16 |  | RTC hour
30033 | 32 | R | U16 |  | RTC minute
30034 | 33 | R | U16 |  | RTC second
30040 | 39 | R | U16 | bitmask | Outputs bitmask (bit0=CH1 … bit15=CH16)
30041 | 40 | R | U16 | bitmask | Inputs bitmask (bit0=IN1 … bit15=IN16)
30042 | 41 | R | U16 | bitmask | Direct inputs bitmask (bit0..2 used)
30043 | 42 | R | U16 | bitfield | System status flags (bit0=ETH,1=WiFi,2=AP,3=MasterEn,4=RestartReq,5=ModbusRun)

## HoldingRegisters
Ref | Offset (0-based) | R/W | Type | Units/Format | Description
40001 | 0 | R | U16 | 0x0100 | Register map version
40002 | 1 | R | U16 | 0xA016 | Device model code
40003 | 2 | R | U16 | MMmm | Firmware version packed (major<<8 ¦ minor)
40004 | 3 | R | U16 | MMmm | Hardware version packed (major<<8 ¦ minor)
40005 | 4 | R | U16 |  | Year of development
40006 | 5 | R | U16 | bitmask | Capabilities bitmask (bit0=Eth,1=WiFi,2=Web,3=WS,4=RS485,5=Modbus,6=RTC,7=Sensors,8=Analog,9=Schedules)
40011..40026 | 10..25 | R/W | STRING(32) | ASCII | Board Name
40027..40042 | 26..41 | R/W | STRING(32) | ASCII | Serial Number
40043..40058 | 42..57 | R | STRING(32) | ASCII | Manufacturer = Microcode Engineering
40059..40066 | 58..65 | R | STRING(16) | ASCII | Firmware version string
40067..40074 | 66..73 | R | STRING(16) | ASCII | Hardware version string
40075..40090 | 74..89 | R/W | STRING(32) | ASCII | Device Name (matches web UI device name)
40101..40106 | 100..105 | R | U16 bytes | 0..255 | EFUSE MAC bytes
40107..40112 | 106..111 | R/W | U16 bytes | 0..255 | Ethernet MAC config bytes
40113..40118 | 112..117 | R/W | U16 bytes | 0..255 | WiFi STA MAC config bytes
40119..40124 | 118..123 | R/W | U16 bytes | 0..255 | WiFi AP MAC config bytes
40201 | 200 | R/W | U16 | 0=custom,1=Modbus | RS485 protocol
40202 | 201 | R/W | U16 | 1..247 | Modbus Slave ID
40203 | 202 | R/W | U16 |  | Baud rate
40204 | 203 | R/W | U16 | 7/8 | Data bits
40205 | 204 | R/W | U16 | 0=N,1=O,2=E | Parity
40206 | 205 | R/W | U16 | 1/2 | Stop bits
40207 | 206 | R/W | U16 | ms | Frame gap ms (suggest 4..10)
40208 | 207 | R/W | U16 | ms | Internal modbus timeout ms (device-side)
40209 | 208 | W | U16 | 0xA55A | APPLY+SAVE serial settings
40210 | 209 | R | U16 | 0=idle,1=ok,2=err | Apply status
40211 | 210 | R/W | U16 |  | USB baud rate
40212 | 211 | R/W | U16 |  | USB data bits
40213 | 212 | R/W | U16 |  | USB parity
40214 | 213 | R/W | U16 |  | USB stop bits
40301 | 300 | R/W | U16 | bitmask | Outputs bitmask write
40302 | 301 | R/W | U16 | bitmask | Outputs write mask
40303 | 302 | R | U16 | bitmask | Current outputs bitmask (mirror of IR30040)
40304 | 303 | R | U16 | bitmask | Current inputs bitmask (mirror of IR30041)
40311..40318 | 310..317 | R/W | FLOAT32×4 | 2 regs/float | Analog scale factor CH1..CH4
40319..40326 | 318..325 | R/W | FLOAT32×4 | 2 regs/float | Analog offset CH1..CH4
40610 | 609 | W | U16 | 0xA55A | CMD_ARM (two-step command)
40611 | 610 | W | U16 |  | CMD_CODE (1=Reboot,2=Save,3=Reload,4=FactoryDefaults)
40612 | 611 | W | U16 |  | CMD_ARG0
40613 | 612 | W | U16 |  | CMD_ARG1
40614 | 613 | W | U16 | 0x5AA5 | CMD_CONFIRM (exec if armed)
40615 | 614 | R | U16 | 0=idle,1=armed,2=running,3=done_ok,4=done_err | CMD_STATUS
40616 | 615 | R | U16 |  | CMD_RESULT
40617 | 616 | R | U16 |  | CMD_LAST_ERROR